## Cover
Feasibility and design:
Lighting intervention estimator
Should further information be required, please contact us at:
psdecarbguidance@es.catapult.org.uk
Licence and disclaimer
This document has been prepared by Energy Systems Catapult Limited (“ESC”) working on behalf of Department for Energy Security and Net Zero ("DESNZ") and Government Property Function (“GPF”).
The document and its contents have been prepared in good faith, based upon the information available to ESC at the time of writing and are made available “as is” without any representations, conditions, warranties or other terms of any kind. The ESC and the authors, together with DESNZ, GPF, their employees, directors, servants or agents exclude to the maximum extent permissible by law all representations, warranties, conditions or other terms whatsoever (whether express or implied) regarding the use of this document or its content including any warranties of title, merchantability, accuracy, completeness, non-infringement or that the document or its contents are of satisfactory or any particular quality or fit for any particular purpose.
Any person accessing this document and using it, or any of its contents, is solely responsible for determining the appropriateness of any reliance put on it and assumes all risks in doing so.
All content of this document is copyright © 2023 Energy Systems Catapult Limited. The information in this document is the property of the ESC. You may copy, publish, distribute or otherwise transmit the information PROVIDED THAT you acknowledge that the information contains copyright information of the ESC and include the following acknowledgement “Information taken from Lighting intervention estimator created by the Energy Systems Catapult Limited”.

## User Notes - Read Me
Feasibility and design:
Lighting intervention estimator
Guidance
This estimator is designed to provide an estimation of costs and energy efficiency benefits of upgrading existing lighting to light-emitting diode (LED) lighting on a campus style site or at an organisational portfolio level. Using this estimator also provides a repository of site information to be assembled in a consistent format. This guidance is produced as part of the development of a consistent approach to assessing decarbonisation for scaled delivery.
This tool can be used standalone or as part of the Public Sector Decarbonisation Guidance feasibility and design process to assess the impact of installing LEDs on a given site's energy usage. It provides an estimation of the financial cost as well as the energy and cost savings to upgrade a site's lighting.
LED lighting will generally pay back well, and within a few years. Where applicable, a lighting retrofit programme for a whole site should be considered, only omitting areas where payback seemed excessive (e.g. >10 years). Note that a proportion of the costs of routine replacement of existing lighting will be saved due to the longer operating lifetime of LED lights. Therefore the frequency of replacement, based on bulb lifetimes and operating hours, and an additional cost of £5/m2 are added to account for labour and administration costs of routine bulb replacement based on the proportion of total floor area per year. Power required for existing and LED replacement lighting will depend on the existing lighting level required as well as the existing lighting type. These are input based on the site specific information and form the basis of the estimations provided.
General Notes
1) All salmon pink cells are for user input
2) All blue cells are automatically calculated based on user input and data from assumptions
Tabs
The LED Lighting Estimator tab is the main calculator as described below.
The Savings Hours tab provides estimates of when in the day energy might be saved for use in site energy modelling within engineering analyses.
The User Data Sources and Assumptions tab should be used by the tool user to record the sources and file locations of data used to populate this model for future reference.
Model Details - LED Lighting Model tab
1) Select site organisation type from drop-down menu. Categories have been defined based on their energy use and relative site size: • Low-density (applicable to sites within a rural setting that are less constrained - costs based off our MOD references); • Standard (applicable to majority of sites within an urban setting and varying complexity - costs based off our NHS references); or • High-security (applicable to sites where additional security measures are required, e.g. prisons - costs based off our MOJ references)
2) Enter site electricity cost, site labour cost to replace a fitting, and survey cost per building - plus any additional cost percentages. Default estimate values are provided as standard if site data is not available
3) Complete details for building across different parts of the site, separating out any sub-areas
4) Enter floor area for each site sub-area
5) Select Area type (this gives a broad breakdown of lighting requirements based on CIBSE Part F) and sub-type (used in LED installations calculations) from drop-down lists
6) Select current lamp type. Note that High Pressure Sodium is not available for "Commercial" and Compact Fluorescent is not available for "Industrial" area use category (as a baseline examples did not exist for these scenarios)
7) Select current lighting density (this reflects different levels of lighting detailed in CIBSE Part F). Note that for "Commercial" area use category the maximum density available is 750 lux, whereas for "Industrial" it is 1,000 lux
8) Set current light on time and days per week operation. Note that for some buildings a single line item in the model could contains areas with different lighting times. A calculation of the weighted average time is provided which can be adapted to suit site particulars
9) Set whether upgrade includes lighting controls
10) Calculations for each area are performed in blue
11) Results for the whole site are provided. Additional cost percentages for Prelims etc. are only added to the Total LED installation costs. They are not added to individual line item costs. Total site values will therefore not be an exact match to the sum of the individual line items
12) A cross reference to the Building Energy Efficiency Survey (BEES) 2014-15 data is available for comparisons / reference, by selecting the BEES Building Use Category and BEES Lighting Use Category. BEES set out to improve and update the evidence of how energy is used, and to provide an assessment of the abatement opportunities for all non-domestic premises across England and Wales
User Notes
Use the BEES calculation as a comparison on current energy use and ROI. Note that BEES surveys were completed several years ago and are unlikely to have included significant LED use. This means that both energy savings and costs from BEES are likely to be lower than those shown through LED replacement.
If the lighting energy use calculated by the model seems high consider adjusting the usage hours to lower values. Remember that very few areas (even in facilities that operate 24/7) will have the lights on 24 hours a day. For example, most hospital wards are dark overnight to allow patients to rest.
Unit costs used in this estimator for different types of lighting have been estimated using real life installation examples carried out in 2020. These have been adjusted and compound inflation has been added to represent expected 2023 pricing. To do this, two years of CPI have been applied (2.5% for 2021 and 7.9% for 2022) - Source: ONS Inflation and Price Indices.
Ensure that all line items have cost values calculated. The sub categories influence costs and are dependent on the organisation selected. If the organisation has been changed then the sub categories may be inappropriate and costs may not be calculated correctly.
Note that within the Savings Hours tab, savings for 4 hour operation are assumed to be spread over an 8 hour day.

## LED Lighting Estimator
LED Lighting Estimator
Site reference | Site Data
| Site Organisation type | Standard
Average hours calculator
Cost details | Site Data | Default value |  |  |  | Building | Areas
| Electricity cost (£/kWh) | 0.112 |  |  |  |  | Common Room | Corridors | Rooms
| Cost to Replace Bulb (£) | 5 |  |  |  | Hours of lighting | 24 | 14 | 5
| Site Survey Cost(£/m2) | 0.29 |  |  |  | Percentage footprint | 15% | 15% | 70%
| Preliminaries | 10% |  |  |  | Weighted Hours average | 9.2
| Contingency | 15%
| Design | 5%
| Site Management | 5%
[12 empty] | Site Totals | [13 empty] | Site Totals
Totals | [11 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 |  |  | 0 | 0 | 0 | 0 | #DIV/0!
Building | Room Location / Identifier | Floor Area (m2) | Area Use Category | Use Sub Category | Installed Lamp Type | Lighting Density (Lux) | Usage (hours per day) | Usage (days per week) | Controls Added in Upgrade | Current Power (kW) | LED Power (kW) | Current Annual Energy (kWh) | LED Annual Energy (kWh) | Current Annual Replacement Rate | LED Annual Replacement Rate | Current Annual Energy Cost (£) | LED Annual Energy Cost (£) | LED Installation Cost (£) | Total Installation Cost (£) | Current Annual Replacement Cost (£) | LED Annual Replacement Cost (£) | ROI (years) | Carbon Reduction (kgCO2e/annum) | BEES Category | BEES Lighting Category | BEES Base Annual Energy Consumption (kWh) | BEES Annual Energy Saving (kWh) | BEES Energy Saving Value (£) | BEES Installation Cost(£) | BEES ROI (years)
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - | 0 | 0 | 0 | 0
Note on D5: Select appropriate site type from drop-down menu. Refer to User Notes for descriptions
Note on D7: Change if known/applicable
Note on K6: Example figures used for sites to provide weighted hours (for entry into column I) where lighting hours vary within a building. Can be changed when this information is known using the salmon cells, otherwise assume whole building is single usage
Note on T18: Excluding design, prelims, contingency, survey and management costs
Note on U18: Including all additional costs for LED installation as given in Site Data (column D) - design, prelims, contingency, survey and management costs
Note on AG17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: is this cell supposed to look like this?

## Saving Hours
Saving Hours
Hours per Day | Annual Energy Savings [kWh] | Hourly Energy Saving [kWh] | Hour Start Saving | Hour End Saving
4 | 0 | 0 | 9:00 | 17:00
8 | 0 | 0 | 9:00 | 17:00
10 | 0 | 0 | 8:00 | 18:00
12 | 0 | 0 | 7:00 | 19:00
18 | 0 | 0 | 6:00 | 24:00
24 | 0 | 0 | 0:00 | 0:00

## User Data Sources Assumptions
User Data Sources and Assumptions
Input | Notes on data sources & assumptions | Link
Preliminaries
Contingency
Design
Site Management
Electricity cost (p/kWHh)
Cost to Replace Bulbs (£/m2)
Site Survey Cost(£/m2)
Total site electricity consumption (kWh)
Building
Room Location / Identifier
Floor Area (m2)
Area Use Category
Use Sub Category
Installed Lamp Type
Lighting Density (Lux)
Useage (hours per day)
Controls Added in Upgrade

## Version Control
Version Control
Version Number | Date Produced | Owner Initials | Key Changes
1 | 2021-12-09 | MA | Initial Release
2 | 2023-01-20 | MA | Addition of carbon reduction per annum, guidance updates and updated costs

## LED Costs (hidden)
Note that these costs included controls.
LED
| Area Use Category | Cost / W | Source
Low_Density | Accommodation | 6.7924 | ESC internal reference | https://www.ons.gov.uk/economy/inflationandpriceindices/timeseries/l55o/mm23
Low_Density | Catering | 4.9495 | ESC internal reference | 2021 | 2.5%
Low_Density | Classroom/training | 4.6118 | ESC internal reference | 2022 | 7.9%
Low_Density | Medical centre | 6.8772 | ESC internal reference |  | 110.6% | compound inflation
Low_Density | Offices | 5.5534 | ESC internal reference
Low_Density | Other | 5.5299 | ESC internal reference
Low_Density | Sports Pool | 5.5067 | ESC internal reference
Low_Density | Workshop | 3.92 | ESC internal reference
Standard | Classroom/training | 3.9403 | ESC internal reference
Standard | Clinics | 4.2159 | ESC internal reference
Standard | Offices | 3.2279 | ESC internal reference
Standard | Wards | 4.3908 | ESC internal reference
Standard | Workshop | 3.92 | ESC internal reference
High_Security | Prison Category B | 5.3518 | ESC internal reference
High_Security | Prison Category C | 5.8568 | ESC internal reference
High_Security | Prison Category D | 5.9933 | ESC internal reference
High_Security | Workshop | 3.92 | ESC internal reference

## Emission factors (hidden)
Emissions | Gross | kgCO2e/kWh
Source | Scope | GHG reporting 2022
Electricity Grid | Scope 2 | 0.19338

## Lighting Power Density (hidden)
Application | Lamp Type | Task illuminance (Lux) | Lighting Density | Power (W/m2) | Lifetime | Source for all except lifetimes | Use Sub Category | Typical Illuminance (lux)
Commercial (offices, shops, schools) | Fluorescent (triphosphor) | 300 | Low | 7 | 12500 | CIBSE Guide F Table 9.1 | Accommodation | 200
Commercial (offices, shops, schools) | Fluorescent (triphosphor) | 500 | Medium | 11 | 12500 | CIBSE Guide F Table 9.1 | Catering | 500
Commercial (offices, shops, schools) | Fluorescent (triphosphor) | 750 | High | 17 | 12500 | CIBSE Guide F Table 9.1 | Classroom/training | 500
Commercial (offices, shops, schools) | Compact Fluorescent | 300 | Low | 8 | 12000 | CIBSE Guide F Table 9.1 | Medical centre
Commercial (offices, shops, schools) | Compact Fluorescent | 500 | Medium | 14 | 12000 | CIBSE Guide F Table 9.1 | Offices | 400
Commercial (offices, shops, schools) | Compact Fluorescent | 750 | High | 21 | 12000 | CIBSE Guide F Table 9.1 | Other
Commercial (offices, shops, schools) | Metal halide | 300 | Low | 11 | 10000 | CIBSE Guide F Table 9.1 | Sports/Pool | 300
Commercial (offices, shops, schools) | Metal halide | 500 | Medium | 18 | 10000 | CIBSE Guide F Table 9.1 | Workshop | 500
Commercial (offices, shops, schools) | Metal halide | 750 | High | 27 | 10000 | CIBSE Guide F Table 9.1
Commercial (offices, shops, schools) | LED | 300 | Low | 3 | 50000 | EST Lighting Guide - The Right Light (see "LED Power Calculations" tab)
Commercial (offices, shops, schools) | LED | 500 | Medium | 5 | 50000 | EST Lighting Guide - The Right Light (see "LED Power Calculations" tab) | Assumed percentage circulation (100lx)
Commercial (offices, shops, schools) | LED | 750 | High | 7.5 | 50000 | EST Lighting Guide - The Right Light (see "LED Power Calculations" tab)
Industrial and Manufacturing | Fluorescent (triphosphor) | 300 | Low | 6 | 12500 | CIBSE Guide F Table 9.1
Industrial and Manufacturing | Fluorescent (triphosphor) | 500 | Medium | 10 | 12500 | CIBSE Guide F Table 9.1
Industrial and Manufacturing | Fluorescent (triphosphor) | 750 | High | 14 | 12500 | CIBSE Guide F Table 9.1
Industrial and Manufacturing | Fluorescent (triphosphor) | 1000 | Maximum | 19 | 12500 | CIBSE Guide F Table 9.1 | Info from Bristol Hospital lighting survey
Industrial and Manufacturing | Metal halide | 300 | Low | 7 | 10000 | CIBSE Guide F Table 9.1 | Building | W/m2 (current) | Lux (current) | W/m2 (LED) | Lux (LED) | Hours use
Industrial and Manufacturing | Metal halide | 500 | Medium | 12 | 10000 | CIBSE Guide F Table 9.1 | Childrens Hospital | 6 | 300 | 1 | 300 | 24
Industrial and Manufacturing | Metal halide | 750 | High | 16 | 10000 | CIBSE Guide F Table 9.1 | Education Centre | 12 | 500 | 3 | 300 | 12
Industrial and Manufacturing | Metal halide | 1000 | Maximum | 23 | 10000 | CIBSE Guide F Table 9.1 | Bristol Trust HQ | 13 | 750 | 4 | 500 | 12
Industrial and Manufacturing | High Pressure Sodium | 300 | Low | 6 | 18000 | CIBSE SLL LGO1 Lighting guide Table 2.2 | Bristol Royal Infirmary (including Queens Building & King Edward) | 4 | 300 | 1 | 300 | 24
Industrial and Manufacturing | High Pressure Sodium | 500 | Medium | 11 | 18000 | CIBSE SLL LGO1 Lighting guide Table 2.2 | Haematology & Oncology | 4 | 300 | 1 | 300 | 24
Industrial and Manufacturing | High Pressure Sodium | 750 | High | 16 | 18000 | CIBSE SLL LGO1 Lighting guide Table 2.2 | Eye & Chapter | 7 | 300 | 2 | 300 | 12
Industrial and Manufacturing | High Pressure Sodium | 1000 | Maximum | 21 | 18000 | CIBSE SLL LGO1 Lighting guide Table 2.2 | Heart Institute inc Sterile & Dermatology | 4 | 300 | 1 | 300 | 24
Industrial and Manufacturing | LED | 300 | Low | 3 | 50000 | EST Lighting Guide - The Right Light (see "LED Power Calculations" tab) | St Michaels Hospital | 3 | 300 | 1 | 300 | 24
Industrial and Manufacturing | LED | 500 | Medium | 5 | 50000 | EST Lighting Guide - The Right Light (see "LED Power Calculations" tab)
Industrial and Manufacturing | LED | 750 | High | 7.5 | 50000 | EST Lighting Guide - The Right Light (see "LED Power Calculations" tab)
Industrial and Manufacturing | LED | 1000 | Maximum | 10 | 50000 | EST Lighting Guide - The Right Light (see "LED Power Calculations" tab)
Info from Healthcare lighting levels guide
[7 empty] | Area, unit or department | Service illuminance (lux)
Accident and emergency
[7 empty] | Reception | 300
[7 empty] | General examination areas | 500
[7 empty] | Circulation/communal areas | 150-300
[7 empty] | Dentistry | 500
General treatment areas
[7 empty] | Autopsy rooms and mortuaries | 500
[7 empty] | Consultation/examination rooms | 500
[7 empty] | Nurse stations | 300
[7 empty] | Operating theatres | 300-500
[7 empty] | Outpatients | 300
[7 empty] | Wards and bedded areas | 300
[7 empty] | Maternity | 300
Note on F2: Grant Tuff: See Detailed lighting model for sources: http://my.hdle.it/78314258

## Other Costs (hidden)
Bulb Type | Lighting Density | Task illuminance (Lux) | Typical Lumen | Typical Cost / Unit | Cost £/m2 | Source
Fluorescent (triphosphor) | Low | 300 | 800 | 4.6009 | 1.7253 | https://www.lyco.co.uk/crompton-9w-warm-white-led-t8-full-glass-tube-2ft.html | https://www.ons.gov.uk/economy/inflationandpriceindices/timeseries/l55o/mm23
Fluorescent (triphosphor) | Medium | 500 | 2850 | 5.0543 | 0.88672 | https://www.lyco.co.uk/osram-t8-s-a-d-fluorescent-tube-36w.html | 2021 | 2.5%
Fluorescent (triphosphor) | High | 750 | 3700 | 5.0543 | 1.0245 | https://www.lyco.co.uk/osram-t8-s-a-d-fluorescent-tube-58w.html | 2022 | 7.9%
Fluorescent (triphosphor) | Maximum | 1000 | 6200 | 4.3686 | 0.70461 | https://www.lyco.co.uk/philips-70w-white-master-tl-d-super-80-t8-fluorescent-tube-6ft.html |  | 110.6% | compound inflation
Compact Fluorescent | Low | 300 | 600 | 3.4949 | 1.7474 | https://www.lyco.co.uk/9w-2-pin-biax-s-g23-cool-white.html
Compact Fluorescent | Medium | 500 | 1200 | 3.6718 | 1.5299 | https://www.lyco.co.uk/18w-4-pin-biax-de-g24q-2-white.html
Compact Fluorescent | High | 750 | 3200 | 5.7068 | 1.3375 | https://www.lyco.co.uk/42w-4-pin-biax-te-gx24q-4-white.html
Compact Fluorescent | Maximum | 1000 | 4300 | 5.0543 | 1.1754 | https://www.lyco.co.uk/philips-master-57w-4-pin-pl-t-gx24q-5-dimmable.html
Metal halide | Low | 300 | 7000 | 21.1241 | 0.90532 | https://uk.rs-online.com/web/p/metal-halide-lamps/7863252/
Metal halide | Medium | 500 | 33200 | 21.0799 | 0.31747 | https://uk.rs-online.com/web/p/son-lamps/3818517/
Metal halide | High | 750 | 36000 | 21.5223 | 0.44838 | https://uk.rs-online.com/web/p/metal-halide-lamps/6997222/
Metal halide | Maximum | 1000 | 90000 | 34.064 | 0.37849 | https://uk.rs-online.com/web/p/metal-halide-lamps/7899927/
High Pressure Sodium | Low | 300 | 4400 | 12.7851 | 0.87171 | https://www.bltdirect.com/son-t-plus-tubular-external-ignitor-50-watt-es
High Pressure Sodium | Medium | 500 | 10500 | 14.0016 | 0.66674 | https://www.bltdirect.com/son-t-plus-tubular-external-ignitor-100-watt-ges
High Pressure Sodium | High | 750 | 55000 | 23.7674 | 0.3241 | https://www.bltdirect.com/son-t-plus-tubular-external-ignitor-400-watt-ges-1
High Pressure Sodium | Maximum | 1000 | 130000 | 48.1873 | 0.37067 | https://www.bltdirect.com/son-t-tubular-external-ignitor-1000-watt-ges

## BEES Data (hidden)
Table C.5: Mean electrical energy intensity by energy end use category and community, arts & leisure sub-sector, 2014—15
Years: 2014 to 2015
Coverage: England and Wales
Use Category | Cafes | Clubs & Community centres | Cold stores | Fire/ambulance services | Hairdressers & beauty salons | Health centres | Higher education - residential | Higher education – teaching & research | Hospitals | Hotels | Large distribution warehouses | Large food shops | Large non-food shops | Law courts | Leisure centres | Military accommodation | Military offices | Military storage | Museums | Nurseries | Nursing homes | Offices (private) | Offices (public) | Places of worship | Police stations | Prisons | Pubs | Restaurants & takeaways | Retail warehouses | Showrooms | Small shops | State Primary schools | State Secondary schools | Stores | Theatres | Warehouses | Workshops
All sub-sectors (kWh/m2/year) | 360 | 111 | 460 | 87 | 285.2013 | 85 | 300 | 1660 | 142 | 140 | 90 | 403.428 | 158.2591 | 82 | 159 | 94 | 89 | 22 | 107 | 160 | 120 | 165 | 129 | 23 | 89 | 81 | 160 | 680 | 155.2159 | 102.5725 | 169.5676 | 1140 | 1660 | 40 | 126 | 40 | 47
Display | - | - | - | 3 | 13.4101 | - | 10 | 20 | - | - | - | 19.3047 | 25.8754 | - | 0 | 2.2442 | 0 | 0 | 7 | 0 | - | 0 | - | - | - | 2 | - | - | 22.5908 | 1.2955 | 1.6192 | 0 | 0 | - | 3 | - | -
External | 0 | 2 | 8 | 2 | 0.10421 | - | 0 | 20 | 1 | 1 | 9 | 2.6302 | 1.0092 | 1 | 7 | 0.1759 | 0.67777 | 0.31656 | 2 | 10 | 4 | 3 | 2 | 1 | 3 | 2 | 2 | 3 | 1.5896 | 7.93 | 1.2489 | 30 | 20 | 1 | 2 | 1 | 4
Internal | 20 | 17 | 40 | 29 | 82.1901 | 28 | 60 | 390 | 25 | 20 | 20 | 39.9596 | 52.897 | 17 | 25 | 17.6319 | 37.3239 | 12.0348 | 20 | 50 | 20 | 22 | 21 | 5 | 36 | 20 | 20 | 30 | 75.8161 | 37.4089 | 31.9997 | 330 | 550 | 10 | 27 | 20 | 26
Display | 0 | 0 | 0 | 0.034483 | 0.04702 | 0 | 0.033333 | 0.012048 | 0 | 0 | 0 | 0.047852 | 0.1635 | 0 | 0 | 0.023874 | 0 | 0 | 0.065421 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024691 | 0 | 0 | 0.14554 | 0.01263 | 0.0095488 | 0 | 0 | 0 | 0.02381 | 0 | 0
External | 0 | 0.018018 | 0.017391 | 0.022989 | 0.00036539 | 0 | 0 | 0.012048 | 0.0070423 | 0.0071429 | 0.1 | 0.0065197 | 0.0063768 | 0.012195 | 0.044025 | 0.0018713 | 0.0076154 | 0.014389 | 0.018692 | 0.0625 | 0.033333 | 0.018182 | 0.015504 | 0.043478 | 0.033708 | 0.024691 | 0.0125 | 0.0044118 | 0.010241 | 0.077311 | 0.0073654 | 0.026316 | 0.012048 | 0.025 | 0.015873 | 0.025 | 0.085106
Internal | 0.055556 | 0.15315 | 0.086957 | 0.33333 | 0.28818 | 0.32941 | 0.2 | 0.23494 | 0.17606 | 0.14286 | 0.22222 | 0.09905 | 0.33424 | 0.20732 | 0.15723 | 0.18757 | 0.41937 | 0.54703 | 0.18692 | 0.3125 | 0.16667 | 0.13333 | 0.16279 | 0.21739 | 0.40449 | 0.24691 | 0.125 | 0.044118 | 0.48846 | 0.36471 | 0.18871 | 0.28947 | 0.33133 | 0.25 | 0.21429 | 0.5 | 0.55319
Abatement Potential % | 0.034483 | 0.086957 | 0.020408 | 0.22727 | 0.17143 | 0.19672 | 0.1 | 0.11446 | 0.1009 | 0.067308 | 0.11454 | 0.052189 | 0.18848 | 0.1 | 0.11278 | 0.12 | 0.24528 | 0.36364 | 0.090909 | 0.1875 | 0.1125 | 0.086464 | 0.096618 | 0.15909 | 0.24138 | 0.18919 | 0.067227 | 0.021563 | 0.26291 | 0.26126 | 0.12121 | 0.15789 | 0.18072 | 0.175 | 0.095238 | 0.24802 | 0.27778
Abatement Cost (£/kWh) | 0.36 | 0.419 | 0.15 | 0.278 | 0.295 | 0.34583 | 0.58 | 0.51368 | 0.28821 | 0.33286 | 0.41846 | 0.36065 | 0.49056 | 0.5 | 0.33933 | 0.3 | 0.24846 | 0.405 | 0.35 | 0.53333 | 0.41111 | 0.43807 | 0.429 | 1.4186 | 0.31143 | 0.28714 | 0.43438 | 0.36625 | 0.43554 | 0.38724 | 0.45919 | 0.71611 | 0.503 | 0.77 | 0.3 | 0.4434 | 0.27089

## Control Benefit (hidden)
Assumed lowest benefits from table 1
Lifetime from CIBSE Guide M (p.12-21)
| Break room | 0.17
| Classroom | 0.52
| Conference Room | 0.39
| Office | 0.28
| Restroom | 0.47
| Area Use Category | Saving | Lifetime | Cost (£/m2)
Low_Density | Accommodation | 0.17 | 10 | 3.9262 | https://www.ons.gov.uk/economy/inflationandpriceindices/timeseries/l55o/mm23
Low_Density | Catering | 0.17 | 10 | 3.9262 | 2021 | 2.5%
Low_Density | Classroom/training | 0.52 | 10 | 3.9262 | 2022 | 7.9%
Low_Density | Medical centre | 0.17 | 10 | 3.9262 |  | 110.6% | compound inflation
Low_Density | Offices | 0.28 | 10 | 3.9262
Low_Density | Other | 0.17 | 10 | 3.9262
Low_Density | Sports Pool | 0.17 | 10 | 3.9262
Low_Density | Workshop | 0.17 | 10 | 3.9262
Standard | Classroom/training | 0.52 | 10 | 3.9262
Standard | Clinics | 0.17 | 10 | 3.9262
Standard | Offices | 0.28 | 10 | 3.9262
Standard | Wards | 0.17 | 10 | 3.9262
Standard | Workshop | 0.17 | 10 | 3.9262
High_Security | Prison Category B | 0.17 | 10 | 3.3185
High_Security | Prison Category C | 0.17 | 10 | 2.6815
High_Security | Prison Category D | 0.17 | 10 | 2.3736
High_Security | Workshop | 0.17 | 10 | 3.9262

## LED Power Calculations (hidden)
Equivalent bulb power from EST Lighting Guide - the right light | Bulb Power
These calculations used to populate table on 'Lighting Power Density' tab
Lumen | Incandescent | Halogen | CFL | LED
450 | 40 | 28 | 9 | 5
800 | 60 | 42 | 13 | 8
1600 | 100 | 70 | 25 | 16
Bulbs / m2 | Lumen |  |  |  | LED W/m2
Lux | 450 | 800 | 1600 |  | 450 | 800 | 1600
300 | 0.66667 | 0.375 | 0.1875 |  | 3.3333 | 3 | 3
500 | 1.1111 | 0.625 | 0.3125 |  | 5.5556 | 5 | 5
750 | 1.6667 | 0.9375 | 0.46875 |  | 8.3333 | 7.5 | 7.5
1000 | 2.2222 | 1.25 | 0.625 |  | 11.1111 | 10 | 10

## Lists (hidden)
Area Use Category | Installed Lamp Type | Lighting Density | Hours | Days | Choice | BEES Use Category | BEES Lighting Category | SiteType | Low_Density | Standard | High_Security
Commercial (offices, shops, schools) | Fluorescent (triphosphor) | 300 | 4 | 1 | Yes | Cafes | Display | Low_Density | Accommodation | Classroom/training | Prison Category B
Industrial and Manufacturing | Compact Fluorescent | 500 | 8 | 2 | No | Clubs & Community centres | External | Standard | Catering | Wards | Prison Category C
| Metal halide | 750 | 10 | 3 |  | Cold stores | Internal | High_Security | Classroom/training | Clinics | Prison Category D
| High Pressure Sodium | 1000 | 12 | 4 |  | Fire/ambulance services |  |  | Medical centre | Offices | Workshop
|  |  | 18 | 5 |  | Hairdressers & beauty salons |  |  | Offices | Workshop
|  |  | 24 | 6 |  | Health centres |  |  | Other
|  |  |  | 7 |  | Higher education - residential |  |  | Sports Pool
[6 empty] | Higher education – teaching & research |  |  | Workshop
Hospitals
Hotels
Large distribution warehouses
Large food shops
Large non-food shops
Law courts
Leisure centres
Military accommodation
Military offices
Military storage
Museums
Nurseries
Nursing homes
Offices (private)
Offices (public)
Places of worship
Police stations
Prisons
Pubs
Restaurants & takeaways
Retail warehouses
Showrooms
Small shops
State Primary schools
State Secondary schools
Stores
Theatres
Warehouses
Workshops